City of Toronto

Long-Term Care Homes & Services

2024 Capital Maintenance Plan

Wesburn Manor

MoHLTC Review Submission

November 2024

Radu Pana, M.SC., P.Eng

Manager, Facilities Management

Seniors Services and Long-Term Care

City of Toronto

205 Cummer Ave,

North York, ON, M2M 2E8

Tel: 416-397-0553

radu.pana@toronto.ca

Table of Contents

- Project Summary

  - Maintenance Projects Overview

  - Air Handling Unit (AHU) Cooling Replacement – Detailed Description

- Operational Plan

  - Overview of Project

  - Administration

  - Communication

  - General Safety Measures

  - Waste Disposal

  - Noise Factors

  - After Hours Work

  - Staff Work Space

  - Summary

        - Project Summary

- Existing Home

Wesburn Manor, located at 400 The West Mall Etobicoke, Ontario, was built in 2002, 4 level building with no basement, with original mechanical system and equipment. There are three (3) mechanical penthouses and roof mounted outdoor condensing units and exhaust fans.

Six (6) AHUs are in MPHs serve the whole building; AHU#1,2,3 & 4 are serving residential rooms. AHU #5 (about 120-ton cooling capacity) serves the core area of the building and most of the office and whole ground floor. AHU #6 is a make-up air unit for main kitchen; Each AHU’s heating is provided by heating water coil, and cooling by cooling coil. Heating is from 4 boilers in MPH which were recently replaced and in good condition, and cooling is by corresponding outdoor condensing unit for each AHU. Motor Control Centres (MCCs) are in each MPH, with main electrical room on ground floor. The system equipment is controlled by BAS.

The facility currently has issues with cooling, AHU#5’s outdoor condensing DX unit has failed and is currently down. Two temporary cooling units, which are provided by Ainsworth, are arranged to supply cooled air to AHU#5.

- Air Handling Unit (AHU) Cooling Replacement – Detailed Description

The purpose of this project is to

- Replace condensing units CD-1,2,3,4,5,6 with air cooled chillers CH-1,2,3

- Replace AHU-1,2,3,4,6 with new AHUs

- Replace the DX cooling coil in AHU-5 with new chilled glycol cooling coil

2) Operational Plan

- Overview of Project

Phasing

Project phasing is not anticipated to be required. Contractor shall perform equipment changeovers with all efforts possible made to minimize equipment downtime.

Permits/Approvals

AHU Cooling replacement project will require building permits.

Hours of Work

Work will take place during regular working hours as defined in the Project Specification and as determined by the Supervisor of Building Services. Unless otherwise specified, hours of work will be standard, between 8am and 5pm.

Anticipated Timelines

The project is estimated to take 6 months to complete. All work will be completed within the 2025 calendar year.

Special Considerations

Contractor will coordinate area of work with Home.

Resident Services Manager will plan and oversee all resident activities.  Resident activities will be relocated to a suitable location depending on daily scheduled work.

Construction and demolition in mechanical penthouse shall be coordinated to reduce the impact the general day to day function of the home.

- Administration

The home’s Administer will be assisted during this project by the home's staff particularly Manager of Building Services. The Engineer for the project is EXP Services Inc. The City of Toronto’s Head Office Project Manager will also manage the Owner’s responsibilities.

In order to facilitate effective and timely communication the following protocols will be in-place:

- Administrative rounds with the Supervisor Building Services and union co-chair of the OH&S Committee as required.

- Communication

Before construction begin, a start-up meeting / orientation will be held with the Contractor and home staff, outlining the requirements imposed on Contractors working in a Long-Term Care environment, and protocols that the Contractor will be expected to follow.  All issues with respect to both resident and staff safety will be identified with staff involvement and will be communicated though formal and informal meetings.

- The Residents’ Council as well as residents and families will be informed of the maintenance projects, expected completion dates and any contingency plan if required.

- All staff will be informed and communicated via general staff meetings and departmental meetings.

- The Administrator or delegate will notify the Ministry of Health and Long-Term Care Regional Office when work is about to begin.

- General Safety Measures

Name of person assigned to monitor safety:

Radu Pana, Manager, Facilities Management

All areas of work will be separated from building users and visitors using barricades and/or hording as required as to the satisfaction of the Building Services Manager and the Engineer.

Each area will be cleaned of debris and construction material frequently during each day and thoroughly cleaned at shift end.

- Barriers / Tool and Equipment Storage

The Contractor must provide temporary measures to ensure all work areas, for all projects, are secure from residents between all working areas and resident spaces.  Dust protection must be incorporated to protect residents and resident spaces from dust exposure.  Tools and equipment must be not be left in areas accessible to residents and must be locked in a secure location when unattended. All tools and equipment shall be stored in a secured location as coordinated with the Building Service Manager.

- Alarms

All door alarms, fire alarms and nurse call devices will operate normally in all areas of the home during the renovation period. Should it be necessary to temporarily bypass a fire zone, a manual fire watch will be implemented.  All fire zones will be restored to full operation at the end of each construction day.

- Housekeeping / Cleanliness

The Contractor shall keep all construction areas clean of construction debris and waste throughout the day.  Housekeeping routines will be adjusted to maintain an acceptable level of cleanliness.  Housekeeping hours will be adjusted, if required, to keep up with the increased demand.

- Transporting Construction Materials

Construction deliveries will be delivered to specific area as coordinated with the Building Service Manager.  All materials that are to be transported throughout the building shall be transported by routes as informed by the Building Service Manager. If required to transport goods and equipment to floor levels not accessible from grade level, the Contractor shall use a dedicated elevator and must coordinate with the home timelines for elevator use to cause minimal disturbances to the home.

- Waste Disposal

Contractor to put a waste bin within the loading area of Long-Term Care Home. Contractor should erect a signage to make sure no mixing on construction and home waste.

- Noise Factors

All reasonable measure will be taken to reduce noise.

Project work will take place during the normal business hours of 8 a.m. to 5 p.m.

- After Hours Work

It is anticipated there will be afterhours work required for dining room floor replacement. There will be no afterhours work in resident rooms and directly adjacent corridors.

- Staff Work Space

It is anticipated that there will be minimal impacts on staff work space.

- Summary

The work outlined in this operational plan will require co-ordination and communication between the Contractor and the Home to ensure the planned improvements are achieved with minimal impact to residents.

When preparing this Operational Plan an emphasis was placed on the resident and staff's comfort and safety. This plan works to minimize impact on the daily lives of the people living and working at each Home by holding Contractors to their schedules and maintaining clear lines of communication between all staff members, residents and families.